MPE Simplexer Controller Specification			Page 1 of 2

The MPE Simplexer Controller shall be designed for simplex pump control operation. The controller’s inputs shall be designed to accept either float switches or a conductance level probe input. The Simplexer Controller shall be UL508 Listed, SCADA ready, and be able to perform either pump-up or pump down control.

The Controller shall be designed to simplify control panel construction by incorporating the following features:

Three Float and/or Conductance Probe Inputs

Level Simulation Pushbutton

HOA Switch

Pump Call and High Level Alarm Relays

Surge Protected Level Inputs

10 Second Power Up Delay

Power On Indicator

Input Level Indicators

Pump  Run Indicator

High-Level Alarm Indicator

Latched High-Level Alarm Indicator

The Controller shall have a 12 pin base to mate with a SD12-PC socket, and have an RS232 Serial Port its MODBUS SCADA connection.

The Push-to-Test push-button shall allow the operator to test the automatic pump call function of the unit, as well as reset the high level alarm. By depressing and holding the Alarm / Push-to-Test Push-button, the unit shall automatically step through the level indications and the pump run and alarm functions. A Push-to-Test feature that only tests the Off and Lead inputs shall not be considered equal.

The level input out-of-sequence logic shall compensate for float switch failure, or skipped level probe input conditions, and allow for continued pump operation. Internal registers shall allow SCADA to monitor Simplexer Controller inputs for an out-of-sequence condition, and shall also allow for the ability to store and reset this information.

The controller shall contain the following setup features, available by accessing the serial port:

Select Pump Up or Pump Down

Select Floats or Level Probe Inputs

Select Sensitivity for Level Probe

Select Alarm Indication Reset (Manual or Automatic)

Select Serial Communication Parameters

MPE Simplexer Controller Specification (continued)			Page 2 of 2

The Controller shall contain the following SCADA features:

Monitor:

Status of Level Inputs

Status of Pump (On/Off)

Status of Push-Button

Run Time via Internal ETM register

Pre-Regulator Power Supply Voltage

Control:

Remotely Reset ETM

Remotely Force Pump On

Remotely Disable Pump

Remotely Reset Alarm

Remotely Reset Fault Code Registers

Fault Codes:

Status of Current Fault Code (if applicable)

Status of Last Fault Code

Status of “Out of Sequence” Registers

The Simplexer Controller, part number 010-120-121P, shall be manufactured by Motor Protection Electronics of Apopka, Florida, (407) 299-3825.

Revision Date: 06/05/2013